CONTENTS

I. Safety Precautions	2

II. IDU Dimensions	4

1.	TMVW wall-mounted unit - dimensional drawing	4

2.	TMCS one-way cassette IDU – dimensional drawing	5

3.	TMCD two-way cassette IDU – dimensional drawing	6

4.	TMCF four-way cassette IDU - dimensional drawing	7

5.	TMDN standard duct IDU - dimensional drawing	8

6.	TMDH high static pressure duct IDU - dimensional drawing	11

7.	TMVX ceiling exposed IDU - dimensional drawing	11

8.	TMDF fresh air processing unit – dimensional drawing	12

9.	TMDP duct IDU – dimensional drawing	12

10.	TP filter module – dimensional drawing	12

III. IDU Installation	14

1.	Installation of TMVW wall-mounted unit	14

2.	Installation of TMCS one-way/TMCD two-way cassette IDU - dimensional drawing	15

3.	Installation of TMCF four-way cassette IDU	17

4.	Installation of TMDN/TMDH/TMDP duct IDU	19

5.	Installation of TMVX ceiling exposed IDU	20

6.	Installation of TMDF fresh air processing unit	20

7.	Duct preparation and installation	22

8.	Selection and installation of IDU electronic expansion valve module	23

9.	Replace the filter module of TP	23

IV. Refrigerant Pipe Connection	25

1.	Principles of refrigerant pipe connection	25

2.	Connection to flared joint of refrigerant pipe	25

3.	Welding of refrigerant pipe	26

4.	Blowing of refrigerant pipe	26

5.	Leakage detecting and insulation of refrigerant pipe	27

V. Drain Pipe Installation	28

1.	Precautions	28

2.	Connection of drainage pipe	28

3.	Centralized drainage	29

4.	Drainage test	30

VI. Electric Control Installation	31

1.	Power supply wiring specifications and precautions	31

2.	Communication line specifications and precautions	31

VII. IDU Code Settings	33

1.	Code typeⅠ	31

2.	Code type II	31

VIII. Precautions When Using/Maintaining Air Conditioner	37

1.	Precautions for air conditioner usage	37

2.	Precautions for air conditioner maintenance	37

3.	Troubleshooting non-air conditioner faults	38

4.	Troubleshooting air conditioner faults	38

IX. After-sales Service of Air Conditioning Unit	40

1.	After-sales service	40

2.	Warranty	40

3.	Repair after warranty period	40

4.	Repair record	40

X. Names and Content of Hazardous Substances in Products	41

I. Safety Precautions

Caution: Read this manual carefully before installation and use of the unit.

This installation manual is applied to TICA TIMS series inverter VRF air conditioning units. The manual is subject to change based on improvement on air conditioners without further notice.

Preparations before installation

Ask the professional technician who has obtained a qualification certificate for air conditioner installation to install the unit. Users are not allowed to install, repair or relocate the air conditioner independently.

Ask the professional electrician who has obtained a qualification certificate to connect electric wires, check whether the line capacity is enough, and whether power cords are damaged, etc.

Install the air conditioning unit following this document. Improper installation may result in water leakage, electric shock or fire.

Precautions during installation

Places unsuitable for installation:

◆ The place where flammable gases or volatile combustibles (e.g., gasoline and combustible dust) may leak and lead to a fire.

◆ The place where acid or alkaline substance or corrosive gas (e.g., sulfur dioxide and hydrogen sulfide) may be produced, easily corroding the unit and leading to refrigerant leakage.

◆ The place where dust, steam, lampblack or special spraying agent is diffused, e.g., a kitchen.

Set a dedicated circuit that complies with the "Electrical equipment engineering standards" and "Indoor electrical wiring specifications".

The unit must be properly grounded. The grounding wire must be reliably connected to the earth. Do not connect the grounding wire to the water pipe, gas pipe, and telephone line.

Use the power cords with enough current capacity and rated power. Do not make the power cords too tight.

All the IDUs and ODUs of the same system must be supplied with power simultaneously.

Securely fix the power cords so that external force is not imposed on the terminal board. If the power cords are not securely connected or fixed, heat is generated, which will cause electric shock or fire.

Electric parts of the unit shall be moisture-proof and far away from the water source. Do not install the wired controller at the places where the flammable gas, sulfide gas, or engine oil is accessible.

Install the drainage pipe according to this manual. Ensure that water will drain smoothly. Take thermal insulation measures well. Prevent generation of condensing water.

When the unit is installed in a small room, take necessary measures to prevent refrigerant concentration from exceeding the limit in case refrigerant leaks.

During installation, if refrigerant leaks, ventilate the room because toxic gas may be generated when refrigerant encounters fire.

After installation, make an air tightness test to check for leak.

For air conditioning units adopting the R410A refrigerant, use the tools and accessories dedicated to R410A.

Precautions at trial operation

Do not operate the wired controller or remote controller with wet hand, or splash water into the wired controller or remote controller.

Do not pull or bend wired controller and centralized wired controller cables forcibly, and do not press the button with sharp objects to avoid abnormal connection.

During the operation of the unit, do not put fingers, sticks, etc., into the air inlet or outlet.

Do not touch refrigerant pipeline during operation or just at the end of operation, as it can lead to scald or frostbite.

Do not turn off power immediately after the unit stops. Wait at least five minutes; otherwise, water leakage may occur.

II. IDU Dimensions

1.	TMVW wall-mounted unit - dimensional drawing

| Model | L (mm) | W (mm) | H (mm) | Condensate drain pipe outer diameter (mm) | Liquid pipe (mm) | Gas pipe (mm) |
| --- | --- | --- | --- | --- | --- | --- |
| TMVW028AB | 970 | 235 | 315 | Φ20 | Φ6.35 | Φ12.7 |
| TMVW036AB |  |  |  |  |  |  |
| TMVW040AB |  |  |  |  |  |  |
| TMVW056AB |  |  |  |  |  |  |
| TMVW063AB | 1100 | 235 | 330 |  |  |  |
| TMVW071AB |  |  |  |  |  | Φ15.88 |

| Model | L (mm) | W (mm) | H (mm) | Condensate drain pipe outer diameter (mm) | Liquid pipe (mm) | Gas pipe (mm) |
| --- | --- | --- | --- | --- | --- | --- |
| TMVW028ACB | 803 | 209 | 287 | Φ20 | Φ6.35 | Φ12.7 |
| TMVW036ACB |  |  |  |  |  |  |
| TMVW040ACB |  |  |  |  |  |  |
| TMVW056ACB | 913 | 209 | 287 |  | Φ9.52 | Φ15.88 |
| TMVW063ACB | 1078 | 257 | 325 |  |  |  |
| TMVW071ACB |  |  |  |  |  |  |

2.	TMCS one-way cassette IDU – dimensional drawing

| Model | A (mm) | B (mm) | C (mm) | D (mm) | E (mm) | F (mm) | G (mm) | H (mm) | I (mm) | Condensate drain pipe outer diameter (mm) | Liquid pipe (mm) | Gas pipe (mm) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| TMCS028A | 1070 | 520 | 916 | 360 | 1030 | 480 | 250 | 870 | 455 | Φ20 | Φ6.35 | Φ12.7 |
| TMCS036A |  |  |  |  |  |  |  |  |  |  |  |  |
| TMCS045A |  |  |  |  |  |  |  |  |  |  |  |  |
| TMCS056A | 1380 | 550 | 1228 | 377 | 1340 | 510 | 290 | 1180 | 485 |  |  |  |
| TMCS071A |  |  |  |  |  |  |  |  |  |  | Φ9.52 | Φ15.88 |

3.	TMCD two-way cassette IDU – dimensional drawing

| Model | A (mm) | B (mm) | C (mm) | D (mm) | Condensate drain pipe outer diameter (mm) | Liquid pipe (mm) | Gas pipe (mm) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| TMCD028A | 1136 | 1008 | 970 | 1176 | Φ20 | Φ6.35 | Φ12.7 |
| TMCD036A |  |  |  |  |  |  |  |
| TMCD045A |  |  |  |  |  |  |  |
| TMCD056A |  |  |  |  |  |  |  |
| TMCD071A | 1376 | 1248 | 1210 | 1416 |  | Φ9.52 | Φ15.88 |
| TMCD080A |  |  |  |  |  |  |  |
| TMCD090A | 1883 | 1728 | 1690 | 1923 |  |  |  |
| TMCD100A |  |  |  |  |  |  |  |
| TMCD125A |  |  |  |  |  |  |  |
| TMCD140A |  |  |  |  |  |  |  |

4.	TMCF four-way cassette IDU - dimensional drawing

B series

Note: The "Top view" in the figure is the actual top view of the unit. For the actual ceiling drilling, perform operations by referring to the "Bottom view" for the drilling installation cardboard in the unit accessories.

| Model | Body height H (mm) | Condensate drain pipe outer diameter (mm) | Liquid pipe (mm) | Gas pipe (mm) |
| --- | --- | --- | --- | --- |
| TMCF028AB/ABB | 230 | φ32 [Note]: The condensate drain pipe outer diameter of TMCF unit body is φ32, the unit accessories contain one φ32-to-φ25 drainage hose, and the drainage pipe of outer diameter φ25 needs to be configured for the project. | Φ6.35 | Φ12.7 |
| TMCF036AB/ABB |  |  |  |  |
| TMCF045AB/ABB |  |  |  |  |
| TMCF050AB/ABB |  |  |  |  |
| TMCF056AB/ABB |  |  |  |  |
| TMCF063AB/ABB |  |  |  |  |
| TMCF071AB/ABB |  |  | Φ9.52 | Φ15.88 |
| TMCF080AB/ABB |  |  |  |  |
| TMCF090AB/ABB | 300 |  |  |  |
| TMCF100AB/ABB |  |  |  |  |
| TMCF112AB/ABB |  |  |  |  |
| TMCF125AB/ABB |  |  |  |  |
| TMCF140AB/ABB |  |  |  |  |
| TMCF160AB/ABB |  |  |  |  |

C series

Note: The "Top view" in the figure is the actual top view of the unit. For the actual ceiling drilling, perform operations by referring to the "Bottom view" for the drilling installation cardboard in the unit accessories.

| Model | Body height H (mm) | Condensate drain pipe outer diameter (mm) | Liquid pipe (mm) | Gas pipe (mm) |
| --- | --- | --- | --- | --- |
| TMCF015AC | 260 | φ25 | Φ6.35 | Φ12.7 |
| TMCF022AC |  |  |  |  |
| TMCF028AC |  |  |  |  |
| TMCF036AC |  |  |  |  |
| TMCF045AC |  |  |  |  |
| TMCF050AC |  |  |  |  |

5.	TMDN standard duct IDU - dimensional drawing

B series

| Model | A (mm) | B (mm) | C (mm) | D (mm) | E (mm) | F (mm) | G (mm) | H (mm) | M (mm) | Condensate drain pipe outer diameter (mm) | Liquid pipe (mm) | Gas pipe (mm) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| TMDN022AB | 673 | 200 | 920 | 290 | 738 | 199 | 988 | 515 | 250 | φ32 [Note]: The condensate drain pipe outer diameter of TMDN-AB unit body is φ32, the unit accessories contain one φ32-to-φ25 drainage hose, and the drainage pipe of outer diameter φ25 needs to be configured for the project. | Φ6.35 | Φ12.7 |
| TMDN025AB |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN028AB |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN032AB |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN036AB |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN040AB |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN045AB | 843 | 200 | 1090 | 290 | 908 | 199 | 1158 | 515 | 250 |  |  |  |
| TMDN050AB |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN056AB |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN063AB |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN071AB | 1143 | 200 | 1390 | 290 | 1208 | 199 | 1458 | 515 | 250 |  | Φ9.52 | Φ15.88 |
| TMDN080AB |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN090AB |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN100AB | 1143 | 242 | 1390 | 329 | 1208 | 241 | 1458 | 557 | 292 |  |  |  |
| TMDN112AB |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN125AB |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN140AB |  |  |  |  |  |  |  |  |  |  |  |  |

C series

| Model | A (mm) | B (mm) | C (mm) | D (mm) | E (mm) | F (mm) | G (mm) | H (mm) | M (mm) | Condensate drain pipe outer diameter (mm) | Liquid pipe (mm) | Gas pipe (mm) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| TMDN022AC/ACB | 510 | 135 | 730 | 390 | 700 | 200 | 810 | 450 | 200 | φ25 | Φ6.35 | Φ9.52 |
| TMDN025AC/ACB |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN028AC/ACB |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN032AC/ACB |  |  |  |  |  |  |  |  |  |  |  | Φ12.7 |
| TMDN036AC/ACB |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN040AC |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN040ACB | 730 |  | 950 |  | 920 |  | 1030 |  |  |  |  |  |
| TMDN045AC/ACB |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN050AC/ACB |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN056AC/ACB |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN063AC/ACB | 950 |  | 1170 |  | 1140 |  | 1250 |  |  |  |  |  |
| TMDN071AC/ACB |  |  |  |  |  |  |  |  |  |  | Φ9.52 | Φ15.88 |

E series

TMDN022~063AEB

| Model | A (mm) | B (mm) | C (mm) | D (mm) | E (mm) | F (mm) | G (mm) | H (mm) | M (mm) | Condensate drain pipe outer diameter (mm) | Liquid pipe (mm) | Gas pipe (mm) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| TMDN022AEB | 730 | 135 | 950 | 390 | 920 | 200 | 1030 | 450 | 200 | Φ25 | Φ6.35 | Φ12.7 |
| TMDN025AEB |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN028AEB |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN032AEB |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN036AEB |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN040AEB |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN045AEB | 950 |  | 1170 |  | 1140 |  | 1250 |  |  |  |  |  |
| TMDN050AEB |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN056AEB |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN063AEB |  |  |  |  |  |  |  |  |  |  |  |  |

TMDN071~160AE

| Model | A (mm) | B (mm) | C (mm) | D (mm) | E (mm) | F (mm) | G (mm) | H (mm) | M (mm) | Condensate drain pipe outer diameter (mm) | Liquid pipe (mm) | Gas pipe (mm) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| TMDN071AE | 1007 | 209 | 1240 | 580 | 1200 | 270 | 1328 | 680 | 270 | φ25 | Φ9.52 | Φ15.88 |
| TMDN080AE |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN090AE |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN100AE |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN112AE |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN125AE |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN140AE |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN160AE |  |  |  |  |  |  |  |  |  |  |  |  |

6.	TMDH high static pressure duct IDU - dimensional drawing

7.	TMVX ceiling exposed IDU - dimensional drawing

| Model | W (mm) | K (mm) | Condensate drain pipe outer diameter (mm) | Liquid pipe (mm) | Gas pipe (mm) |
| --- | --- | --- | --- | --- | --- |
| TMVX028A | 905 | 800 | φ25 | Φ6.35 | Φ12.7 |
| TMVX036A |  |  |  |  |  |
| TMVX056A |  |  |  |  |  |
| TMVX071A | 1288 | 1185 |  | Φ9.52 | Φ15.88 |
| TMVX090A |  |  |  |  |  |
| TMVX112A | 1672 | 1568 |  |  |  |
| TMVX125A |  |  |  |  |  |
| TMVX140A |  |  |  |  |  |

8.	TMDF fresh air processing unit – dimensional drawing

TMDF120, TMDF140

TMDF175, TMDF210, TMDF250, TMDF300

TMDF400, TMDF500, TMDF600

| Model | A (mm) | B (mm) | C (mm) | D (mm) | E (mm) | F (mm) | G (mm) | Condensate drain pipe outer diameter (mm) | Liquid pipe (mm) | Gas pipe (mm) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| TMDF400 | 1690 | 848 | 680 | 1625 | 648 | 940 | 1315 | Φ25 | Φ12.70 | Φ28.58 |
| TMDF500 | 2043 |  |  | 1976 |  | 1062 | 1667 |  | Φ15.88 |  |
| TMDF600 |  |  |  |  |  |  |  |  |  |  |

9、TMDP duct IDU – dimensional drawing

TMDP022~063AEBNNN

| Model | A (mm) | B (mm) | C (mm) | D (mm) | E (mm) | F (mm) | G (mm) | H (mm) | M (mm) | Condensate drain pipe outer diameter (mm) | Liquid pipe (mm) | Gas pipe (mm) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| TMDP022AEBNNN | 730 | 135 | 950 | 390 | 920 | 200 | 1030 | 450 | 200 | Φ25 | Φ6.35 | Φ12.7 |
| TMDP025AEBNNN |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDP028AEBNNN |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDP032AEBNNN |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDP036AEBNNN |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDP040AEBNNN |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDP045AEBNNN | 950 |  | 1170 |  | 1140 |  | 1250 |  |  |  |  |  |
| TMDP050AEBNNN |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDP056AEBNNN |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDP063AEBNNN |  |  |  |  |  |  |  |  |  |  |  |  |

TMDP071~160AEBNNN

| Model | A (mm) | B (mm) | C (mm) | D (mm) | E (mm) | F (mm) | G (mm) | H (mm) | M (mm) | Condensate drain pipe outer diameter (mm) | Liquid pipe (mm) | Gas pipe (mm) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| TMDN071AE | 1007 | 209 | 1240 | 580 | 1200 | 270 | 1328 | 680 | 270 | Φ25 | Φ9.52 | Φ15.88 |
| TMDN080AE |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN090AE |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN100AE |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN112AE |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN125AE |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN140AE |  |  |  |  |  |  |  |  |  |  |  |  |
| TMDN160AE |  |  |  |  |  |  |  |  |  |  |  |  |

10、TP filter module – dimensional drawing

Filter module (TP04BC/ TP06BC)

| Model | A （mm） | B （mm） | C （mm） | D （mm） | E （mm） |
| --- | --- | --- | --- | --- | --- |
| TP04BC | 1176 | 1200 | 230 | 270 | 150 |
| TP06BC |  |  |  |  |  |

Filter module (TP04AA/ TP06AA/TP04AB/TP06AB)

| Model | A （mm） | B （mm） | C （mm） | D （mm） | E （mm） |
| --- | --- | --- | --- | --- | --- |
| TP04AA | 880 | 920 | 160 | 200 | 42 |
| TP06AA |  |  |  |  |  |
| TP04AB | 1100 | 1140 | 160 | 200 | 42 |
| TP06AB |  |  |  |  |  |

III. IDU Installation

Precautions

Carefully hold the lifting point or other force bearing parts when taking the IDU out from the package. Do not apply force to the gas pipe, liquid pipe or drainage pipe.

Install the IDU in a position where the air duct is shorter and the workload is less to facilitate wiring and pipe connection.

Ensure that the installation position is strong enough to bear the IDU weight. Otherwise, it may cause personal injury and machine damage.

Ensure that the lifting screw has enough strength to bear the unit weight. Use at least 4 lifting screws to suspend the IDU.

Ensure good ventilation and airflow to every corner of the room.

To ensure proper airflow, there should not be any obstructions at the air inlet and outlet.

Reserve sufficient space for maintenance and repair. The manhole should be placed at the electric control box side for convenience.

Keep the IDU away from lighting facilities that use ballasts, because the ballasts will trigger reception failure of remote controller.

Avoid direct sunlight.

- The indoor unit shall not be installed in the area not used by air conditioning (that is, shall not be installed outdoors), otherwise there will be leakage or electric shock accidents.

1.	Installation of TMVW wall-mounted unit

1)	Installation position

Install the unit according to parameters listed in the above figure. The unit performance may be somewhat affected if the actual installation is not in full compliance with the requirements.

2)	Unit installation

Measure and mark the position for hanging the IDU.

Remove the under plate on the rear side of the IDU. As indicated by the mark made in step one, use 4 to 6 masonry nails (or steel nails, expansion bolts) to fix the under plate onto the wall.

Drill a φ65mm hole on the wall. Install the unit pipe through the hole.

Hang the IDU on the upper hook of the mounting plate. Slightly push the unit leftward and rightward to verify that the unit is securely placed.

Slightly raise the bottom of the unit, push the unit towards the wall and pull it downward at the same time. Then, try to move the unit in all directions to check if it is securely fixed, as shown in the following figure.

Use a level instrument to check if the unit is placed horizontally.

Connect the refrigerant pipe and drainage pipe.

3)	Precautions

The filter screen shall be easily removed and cleaned.

Ensure that sufficient space for maintenance is reserved around the unit.

If the pipe outlet is at the left or rear left of the unit, place a support between the rear right of the IDU and the wall. After piping connection is finished, remove the support.

Do not place any electrical apparatus, power strip or other object under the unit. Otherwise, drip caused by poor drainage of the unit may contaminate the furniture.

Decide the location of drainage pipe on site. Be aware of the unit's degree of inclination.

2.	Installation of TMCS one-way/TMCD two-way cassette IDU - dimensional drawing

1)	Unit lifting

Measure and mark the place where the unit is located. Drill holes on the ceiling. Install the booms and make sure that the booms are securely fixed.

Use nuts, flat washers and spring washers to install the IDU onto the booms.

Use a level instrument to check if the unit is placed horizontally.

Use an installation gauge to adjust the height of the IDU. The air inlet side should be about 5mm higher than the air outlet side (air inlet: 25mm; air outlet: 20mm). The installation gauge must align to the opening on the ceiling during measuring.

After the IDU is confirmed to be horizontal, fasten the nuts on the booms to prevent the IDU from falling or vibration.

2) Panel installation

(1) Remove the return air grille from the panel. Fix the panel onto the unit body.

Push the sliders on the grille to the left and right sides, and then push them up to open the grille, as shown in Figure 1.

Remove the safety buckles on both sides of the front grille, and then remove the front grille, as shown in Figure 2.

Insert panel hooks into the holes on both sides of the IDU body, as shown in Figure 3.

Install the fixing screws (6 in total) on the panel. Adjust the panel location to ensure that there is no gap between the panel and the ceiling. Then, fasten all the screws, as shown in Figure 4.

Check if the panel is correctly connected to the IDU. If there is a gap between the panel and the ceiling, adjust the height of the IDU body. Incorrect installation of panel on the IDU will lead to air leakage, condensation, drip and other problems.

(2) Respectively connect the connection cable of remote control light board and the connection cable of fan motor on the panel to the corresponding connector in the electric control box of IDU (matching cables have the consistent color).

(3) Install the return air grille back to the panel.

3.	Installation of TMCF four-way cassette IDU

1)	Installation position

Install the unit according to parameters listed in the above figure. The unit performance may be somewhat affected if the actual installation is not in full compliance with the requirements.

2)	Unit lifting

Measure and mark the place where the unit is located. Drill holes on the ceiling. Install the booms (M8 or M10) and make sure that the booms are securely fixed.

Determine the distance between booms, as indicated in the following figure.

Use nuts, flat washers and spring washers to install the IDU onto the booms.

Check to make sure that the installed unit is placed horizontally. Tighten the nut on the boom to prevent the IDU from falling and vibrating.

Check and ensure that the unit body is at the center of the ceiling opening.

3)	B series Panel installation

(1)	Remove the air inlet grille: Hold and push inward the air inlet grille lock, and open the grille in the direction of the arrow ①. Then, remove the grille from the panel in the sequence as indicated by the arrows ② and ③.

(2)	Remove the covers at the four corners of the panel.

(3)	Install the panel:

Align the directions of the fan motor on the panel and the unit body pipe. Attach the shackles (2 in total) on the fan motor side and the diagonal side to the hooks on the unit body, as shown in Figure ①.

Attach the two shackles on the sides adjacent to the fan motor side to the hooks on the unit body, as shown in Figure ②.

Since the covers at the four corners are removed, the hex screws inside are visible. Screw these four hex screws. The panel rises, as shown in Figure ③.

Slightly adjust the panel in the arrow direction as shown in Figure ④, to ensure that the panel properly fits the opening on the ceiling.

Tighten the four hex screws to keep a 5 to 8mm thick insulation between the panel and the unit body.

Note: Hex screws must be fastened. Otherwise, cold air flow leakage, water condensation, water leakage or even electric control box short circuit may occur.

(4)	Connect the connection cable of remote control light board and that of fan motor to the IDU control panel, as shown in the following figure.

4)	C series Panel installation

(1)	Open the air inlet grille: pull the lock of the air inlet grille backward and open the grille in the direction of the arrow ①;

(2)	Install the Panel：

Adjust the panel light board and the fuselage tube to the opposite direction, and install the panel on the drain tray as shown in the figure with the four bolts included in the panel package;

Note: Be sure to make the wiring, and the cable should not be stuck between the body and the panel, otherwise it may cause air leakage and cause condensation and water droplets;

- Tighten the four hex head screws respectively to make the panel firmly fixed on the fuselage, and the thickness of the insulation cotton between the rear panel and the fuselage should be 5-8mm;

- Note: Be sure to tighten the hexagon head screws to avoid air-conditioning leakage, water condensation, water leakage, and even short circuit of the electric control box.

(3)	Connect the connecting wire of the remote control light board and the connecting wire of the wind pendulum motor to the indoor unit control board. As shown below:

(5)	Return air grille installation

Verify that the filter is correctly and securely installed in the return air grille.

Considering the ceiling design and the convenience of opening the grille, install back the return air grille to the panel.

4.	Installation of TMDN/TMDH/TMDP duct IDU

1)	Installation of TMDN standard duct IDU

Ensure a sufficient maintenance space around the unit, as shown above (in the figure: A x B = Unit length x Width).

Determine the place where the unit is located. Install the booms and make sure that the booms are securely fixed.

Check whether the booms are properly aligned with the unit. Install the unit on the booms.

Make sure that the IDU has a tilt to the drainage direction, and tighten the nuts on the booms.

2)	Installation of TMDH high static pressure duct unit

(1)	Precautions

The filter screen shall be easily removed and cleaned.

If the lifting screw is over 1.5 m long, anti-vibration measures must be taken.

Ensure that sufficient space for maintenance is reserved around the unit.

(2)	Unit lifting

Determine the place where the unit is located. Install the booms and make sure that the booms are securely fixed.

Check whether the lifting lug is reliable.

Lift the unit:

a) Mount the lifting lugs of the unit between screw caps 1 and 2 on the lifting screw.

b) Use screw cap 2 to adjust height of the device.

c) Guarantee that the unit is installed horizontally.

d) Tighten screw caps 1 and 3 to prevent the unit from falling off and vibrating.

3)	Installation of TMDP duct unit

- Ensure a sufficient maintenance space around the unit, as shown above (in the figure: A x (B+δ) = Unit length x (Width + filter frame thickness), δ is selected according to the type of screen frame.)

- Determine the place where the unit is located. Install the booms and make sure that the booms are securely fixed.

- Check whether the booms are properly aligned with the unit. Install the unit on the booms.

- Make sure that the IDU has a tilt to the drainage direction, and tighten the nuts on the booms.

- For a better experience, it is recommended that the filter frame adopts back return air type to install and replace it once a year.

5.	Installation of TMVX ceiling exposed IDU

Ensure that sufficient space for maintenance is reserved around the unit, as shown in the right figure.

Determine the place where the unit is located. Install the booms and make sure that the booms are securely fixed.

Remove the return air grille, frame and mounting panel.

Install the mounting panel onto booms.

Attach the unit to the mounting panel and fasten the nuts. Install the refrigerant pipe and drainage pipe. Then, install back the return air grille and frame.

6.	Installation of TMDF fresh air processing unit

1)	Precautions

If the temperature and humidity above the ceiling are expected to exceed 30°C and 80% respectively, apply an insulation layer on the unit body.

Do not share the same ODU with other inverter VRF IDU(s).

Fresh air unit may generate larger noise. Noise mitigation and vibration isolation measures are required sometimes.

A separate fresh air inlet is required. This inlet cannot be set at the air return side of other IDU; otherwise, the return air temperature sensor may not be able to correctly detect the actual indoor temperature.

Reserve sufficient space around the unit for maintenance and repair.

The filter screen shall be easily removed and cleaned.

2)	Unit lifting

Determine the place where the unit is located. Install the booms and make sure that the booms are securely fixed.

Verify that the unit is ready for lifting.

Lift the unit:

a) Mount the lifting lugs of the unit between screw caps 1 and 2 on the lifting screw.

b) Use screw cap 2 to adjust height of the device.

c) Guarantee that the unit is installed horizontally.

d) Tighten screw caps 1 and 3 to prevent the unit from falling off and vibrating.

Notes:

For TMDF120-TMDF300, the parts for lifting are lifting lugs (as shown in the left figure above).

For TMDF400-TMDF600, the parts for lifting are mounting holes of the feet (as shown in the right figure above).

Put the drainage outlet and air intake vent side to a lower position to prevent water leakage, as shown in the following figure:

3)	Duct installation

Connect the duct and inlet/outlet flange.

Use aluminum adhesive belt to seal the connection of inlet flange and duct and that of outlet flange and duct to prevent leakage.

Use screws to connect the inlet/outlet flange to the unit.

Notes:

Make sure that the air intake side of air duct tilts down to prevent water accumulation.

Connect the air duct so that the air intake side can take in outside air; otherwise the unit cannot operate normally.

To prevent condensation, take heat insulation measures for the air duct (material: glass wool or expanded polyethylene; thickness: 25mm).

7.	Duct preparation and installation

1)	Precautions

Design the air channel based on the unit external static pressure. The air channel resistance must be equal to the unit external static pressure. Otherwise, excessive or insufficient air flow may lead to unit malfunction.

The distance between the indoor air return and the heat exchanger's air inlet must be at least 1 m.

Proper duct design could effectively eliminate the noise.

A balance between the unit external static pressure and the pipeline resistance could be reached by changing the fan speed or adjusting the duct resistance (for example, adjust the diffuser's air supply speed).

The return air pipe and air supply pipe must be insulated to minimize energy loss and condensation.

The return air pipe and air supply pipe must be fixed onto the precast slab by iron support. All connections of duct must be sealed.

The distance between the edge of the return air pipe/air supply pipe and the wall must be at least 150mm.

2)	Installation of return air pipe (applicable to TMDN series)

When bottom return air mode is adopted, purchase or make a segment of canvas duct, fold the canvas duct and use it to connect the return air inlet and the return air window. It can be flexibly adjusted to suit the height of the ceiling and avoid ceiling vibration when the unit is running.

When back return air mode is adopted, make a return air pipe and use rivet to connect one end of the pipe to the IDU return air inlet, and connect the other end to the return air window, as shown in the figure below.

3)	Installation of air outlet duct (applicable to TMDN series)

Usually the air outlet duct is of the rectangle or circular type. The rectangle duct can be connected to the IDU air outlet through rivets directly. The circular duct requires adding a transition duct to connect to the IDU air outlet, and the other end can connect to the air outlet window separately or after diversion, as shown below:

The wind speed of each air outlet window should be adjusted basically consistent to meet the room air conditioning requirements.

4)	Duct installation (applicable to TMDH series)

8.	Selection and installation of IDU electronic expansion valve module

Electronic expansion valve module is required for the TMCD-A, TMCS-A, and TMVX-A series. Select the proper electronic expansion valve module according to the "Application identifier of electronic expansion valve module" label attached to the specific IDU.

1)	Precautions

Make sure that the electronic expansion valve module is placed straight up.

The electronic expansion valve module must be installed in the liquid pipe of the corresponding IDU, by screwing the electronic expansion valve module to the flared joint of the liquid pipe.

The inlet of the electronic expansion valve module is connected to the copper pipe from the ODU's liquid pipe, ant the outlet is connected to the IDU's liquid pipe.

The control cable lead from the electronic expansion valve module must be securely connected to the control module of the corresponding IDU.

The pipe connecting the electronic expansion valve module and the IDU should be no longer than 1 m.

The copper pipe connecting the electronic expansion valve module and the IDU must be properly insulated to avoid drip.

2)	Dimensions of electronic expansion valve module

3)	Installation diagram of electronic expansion valve module

9.	Replace the filter module of TP

TMDP series units must be installed with filter module. Please select filter module based on actual requirements  .

1)	Filter replacement method 1

Remove the two screws, then remove the left access plate, pull out the filter screen for replacement.

.

2)	Filter replacement method 2

Remove the two screws, then turn the bottom access plate, pull out the filter screen for replacement.

IV. Refrigerant Pipe Connection

1.	Principles of refrigerant pipe connection

|  | Cause | Preventive measures |
| --- | --- | --- |
| Drying | ● External water intrusion (rain, water supply for construction, etc) | Piping processing → blowing → vacuum drying |
|  | ● Condensate water intrusion from inside the pipe |  |
| Cleanness | ● Oxide generation inside the pipe when welding | Replacement of nitrogen |
|  | ● Dust or other foreign object entering | Blowing |
| Air tightness | ● Incomplete welding | Use proper material → (copper pipe, welding rod) |
|  | ● Flare pipe leak | Operate in strict accordance with relevant requirements on flare pipe usage |
|  | ● Edge leak | Operate in strict accordance with relevant requirements on welding |
|  |  | Operate in strict accordance with relevant requirements on piping |

2.	Connection to flared joint of refrigerant pipe

Use a special cutting tool to cut the pipe. For pipes with too large diameter, a metal cut saw may be used, but make sure to avoid the saw dust from entering the pipe.

Use the delivery-attached flared joint screw cap only. Before flaring, install the screw cap on the copper pipe first.

Verify that the flared joints are concentric, and the surface is free from damage and defects such as burr, crack and wrinkle.

Before connecting the flared joint, apply ester oil or ethereal oil on both sides of the flared joint, and finger-tight the screw cap for 3 to 4 screws.

Fasten the screw cap with a proper torque. Use two wrenches to hold the pipe.

| Diameter (mm) | Torque | Pipe flared joint size A (mm) |
| --- | --- | --- |
| φ6.35 | 14.2-17.2 N•m (144-176 kgf•cm) | 8.7-9.1 |
| φ9.52 | 32.7-39.9 N•m (333-407 kgf•cm) | 12.8-13.2 |
| Φ12.70 | 49.5-60.3 N•m (504-616 kgf•cm) | 16.2-16.6 |
| φ15.88 | 61.8-75.4 N•m (630-770 kgf•cm) | 19.3-19.7 |
| φ19.05 | 92.7-118.6 N•m (990-1210 kgf•cm) | 23.1-23.7 |

3.	Welding of refrigerant pipe

Perform welding downward or horizontally. Avoid overhead welding if possible.

Install the liquid pipe and gas pipe in proper direction and angle to avoid inadequate supply of refrigerant and build-up of oil.

Replacement of nitrogen during welding: During welding, fill 0.02-0.05 MPa nitrogen into the pipe to avoid system block due to oxide generation. After welding, use nitrogen to blow or let it cool down. Do not spray cold water for cooling because cracks will be generated upon sudden cooling of the weld junction.

Try to reduce bended piping and use bends with larger radius.

Requirement for distance between supports of horizontal pipeline is listed in the following table:

| Pipe diameter | < 20mm | 20-45mm | Above 45mm |
| --- | --- | --- | --- |
| Max distance (m) | 1.0 | 1.5 | 2.0 |

4.	Blowing of refrigerant pipe

Entering of dust and moisture into the pipe is unavoidable during installation and construction. Therefore, the pipe must be blown dry with nitrogen after pipe construction is completed.

Use nitrogen for blowing. The nitrogen cylinder should be equipped with a pressure regulating valve.

Use an inflation tube to connect the pressure regulating valve to the inlet on the liquid pipe side of the ODU.

Use blind plugs to block up all copper pipe connectors on the liquid pipe side, except for IDU A.

Open the nitrogen cylinder and set the pressure to 0.5MPa.

Check whether the nitrogen flows through the liquid pipe leading to IDU A (the corresponding connector on the IDU must be sealed with adhesive tape to prevent dirt from entering the pipe).

Blowing:

a)	Use insulating material to block up the liquid pipe of IDU A.

b)	When you feel that you cannot block up the pipe anymore as the pressure increases, remove the insulating material quickly and let the nitrogen release quickly from the pipe (first blowing).

c)	Use insulating material to block up the liquid pipe again (second blowing).

d)	Place a clean cloth at the pipe mouth. You may find the dirt brought out by the nitrogen on the cloth. If the cloth turns a bit damp, it indicates that there is water inside the pipe. Blow the pipe repeatedly until nothing can be blown out and the cloth is no longer damp.

Repeat the above steps on IDU B.

After blowing the liquid pipe, blow the gas pipe.

5.	Leakage detecting and insulation of refrigerant pipe

After piping work is completed, make sure to do air tightness test for the entire refrigeration system (IDU and piping). Fill nitrogen from both the gas pipe and liquid pipe sides simultaneously until the pressure reaches the stipulated value (R410A model: 4.0 MPa). Maintain the pressure for 24 hours. Then, check if the pressure changes. In this way, you can determine the air tightness of the connections (welding joint or flare) and the entire system and find the leak source (if any).

Note: If the temperature during pressure increasing is different from the temperature when observing, adjust according to the following formula:

Actual value = Pressure during pressure increasing + (Temperature during pressure increasing - Temperature when observing) x 0.1 kgf/cm2

When there is no leak, insulate the piping. The gas pipe and liquid pipe need to be insulated separately.

V. Drain Pipe Installation

1.	Precautions

Before installing the drainage pipe, remove the drainage plug on the left or right side of the chassis.

Keep the condensate water pipe as short as possible and make the water drain in a downward direction along the slop (en route). Avoid zigzag layout of the drainage pipe; otherwise, the condensate water may flow backward.

For the installation of horizontal drainage pipe, a slop grade of at least 1/100 should be guaranteed, and the pipe should be fixed with booms every 1.0 to 1.5 m.

The interval of booms for fixing the horizontal drainage pipe is:

| Material | Nominal diameter | Spacing |
| --- | --- | --- |
| Rigid PVC pipe | 25-40mm | Less than 1.5m |

2.	Connection of drainage pipe

1)	When no drain pump is provided:

Do not install the drain pipe upward; otherwise, water may flow back into the machine.

Install a U-shaped water trap at the end of drain pipe for the high static pressure and fresh air handling units to prevent water from flowing back into the IDU, and install a drain cleaning port at the same time.

2)	When a drain pump is provided:

The drainage height outside the unit cannot exceed 500mm; otherwise water may leak.

Raise the drainage pipe by 300 to 500mm, and then lower it for at least 20mm.

3.	Centralized drainage

Please select a drainage pipe diameter matched with the unit operating capacity.

1)	When no drain pump is provided:

2)	When a drain pump is provided:

When more than three IDUs are installed, install the main exhaust port in the front of the IDU farthest from the main drainage pipeline.

4.	Drainage test

After the drainage pipe is installed, check whether water is drained smoothly. Prepare 2 liter water. Inject water to the water tray of the IDU, as shown in the following figure.

For the model configured with a drain pump, run the machine under the cooling mode and check pumping of the drain pump.

Check for water drainage at the end of the drainage pipe. Ensure that condensate water can be smoothly drained and water does not leak at the water drainage position.

After the drainage test is completed, apply insulation materials to the condensing water pipe.

VI. Electric Control Installation

TIMS series inverter VRF air conditioning unit has both high voltage (power) line and control (communications) line. The high voltage line consists of the power of the chiller and that of the IDU; the control line consists of the communications cable for the IDU and ODU and that for the centralized wired controller.

Select cables in accordance with relevant local or national regulations. The model of cable must comply with relevant local and national specifications.

The cables must be securely connected. Do not exert force on the terminal strip.

1.	Power supply wiring specifications and precautions

For the power cable specifications of the chiller, refer to the ODU installation instruction. The power cable specifications of IDU are listed as follows:

| Power supply | Power supply range (V) | Power cord | Earth line |
| --- | --- | --- | --- |
| 220V~/50Hz | 242/198 | ≥1.5mm2 | 1.5mm2 |

Notes:

In case the total power of the IDU exceeds 1700 W (for example, when the electric heater is equipped), adopt the power cable with higher specifications.

The distribution box shall be provided with a set of electric leakage protection device and air switch for each module.

A circuit breaker with larger capacity is required if it is used to connect to multiple IDUs.

If the power cord is damaged, to avoid danger, make sure to ask a professional from the manufacturer or its maintenance department or similar department to replace it.

2.	Communication line specifications and precautions

The 0.75~1.25mm2 shielded twisted pair is used for communications between the IDU, ODU, centralized controller and unit).

Do not connect power line to the connecting terminal of communication cables.

The total length of communication cable is less than 1000 m.

The communication cable, the shield layer and the chiller must be grounded.

Communication cable is well connected before being powered on. Do not remove the power plug with power on, lest the communication chips would be damaged.

To prevent high voltage signal from disturbing control signal, shielded twisted pair must be used. Try to select communication cable with dense shielding layers and smaller lay.

Control signal has two polarities A and B, and different polarities cannot be connected; otherwise, communication failures may be caused, as shown in the figure on the right.

When power line is parallel with the communication cable, they shall be covered by respective conduits and kept at some distance away.

After installation, protect the communication cables of the wired controller or the centralized controller and ensure good connection.

Diagram of IDU and ODU communication cable layout:

VII. IDU Code Settings

IDU capacity code and model code are preset before delivery. Check if they are correct.

There are two types of codes. For details, please refer to the actual air conditioning unit.

1.	Type I

1)	S1: IDU capacity code

(1)	Applicable to IDUs except TMDF

| IDU models | S1 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| TM**015 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |
| TM**022 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 |
| TM**025 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 |
| TM**028 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 |
| TM**032 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |
| TM**036 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 |
| TM**040 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 |
| TM**045 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 1 |
| TM**050 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 |
| TM**056 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 |
| TM**063 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |
| TM**071 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |
| TM**080 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 |
| TM**090 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 0 |
| TM**100 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 |
| TM**112 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 |
| TM**125 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 |
| TM**140 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 |
| TM**160 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |

For example: for model TMCF022, S1 code is 00010110 as below.

(2)	Applicable to TMDF

| IDU models | S1 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| TMDF120A-020 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 |
| TMDF140A-020 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 |
| TMDF175A-022 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 |
| TMDF210A-020 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 |
| TMDF250A-015 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 |
| TMDF250A-020 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 |
| TMDF250A-030 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 |
| TMDF300A-020 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 |
| TMDF400A-020 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |
| TMDF400A-030 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |
| TMDF500A-020 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 |
| TMDF500A-030 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 |
| TMDF600A-020 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 |
| TMDF600A-030 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 |

2)	S2: Address DIP (refer to the actual unit)

| IDU address | Digit 1 | Digit 2 | Digit 3 | Digit 4 | Digit 5 | Digit 6 |
| --- | --- | --- | --- | --- | --- | --- |
| 1# | 0 | 0 | 0 | 0 | 0 | 1 |
| 2# | 0 | 0 | 0 | 0 | 1 | 0 |
| 3# | 0 | 0 | 0 | 0 | 1 | 1 |
| ...... | ...... | ...... | ...... | ...... | ...... | ...... |
| 62# | 1 | 1 | 1 | 1 | 1 | 0 |
| 63# | 1 | 1 | 1 | 1 | 1 | 1 |

3)	S3: Model, function code

| No. |  | Function | 0 | 1 |
| --- | --- | --- | --- | --- |
| S3 Function code | Digit 1 | Remote switch/hotel card | Remote switch | Hotel card |
|  | Digit 2 | Air return temperature selection | Use air return temperature on control panel | Use air return temperature on wired controller |
|  | Digit 3 | Electric heater | Electric heater unavailable | Electric heater available |
|  | Digit 4 | Reserved (set to 0) | / | / |

Note: When hotel card is used, connect the interlock switch to the control panel X8A.

| S3 model code | Digit 5 | Digit 6 | Digit 7 | Digit 8 |
| --- | --- | --- | --- | --- |
| TMDN | 0 | 0 | 0 | 0 |
| TMDH | 0 | 0 | 1 | 0 |
| TMCF | 0 | 0 | 1 | 1 |
| TMVX | 0 | 1 | 0 | 0 |
| TMVW | 0 | 1 | 0 | 1 |
| TMDF | 0 | 1 | 1 | 0 |
| TMCS | 0 | 1 | 1 | 1 |
| TMCD | 1 | 0 | 0 | 0 |

2.	Type II

1)	S1: IDU capacity code

(1)	Applicable to IDUs except TMDF

| IDU models | S1 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| TM**015 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |
| TM**022 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 |
| TM**025 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 |
| TM**028 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 |
| TM**032 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |
| TM**036 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 |
| TM**040 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 |
| TM**045 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 1 |
| TM**050 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 |
| TM**056 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 |
| TM**063 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |
| TM**071 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |
| TM**080 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 |
| TM**090 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 0 |
| TM**100 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 |
| TM**112 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 |
| TM**125 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 |
| TM**140 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 |
| TM**160 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |

For example: for model TMCF022, S1 code is 00010110 as below.

(2)	Applicable to TMDF

| IDU models | S1 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| TMDF120A-020 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 |
| TMDF140A-020 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 |
| TMDF175A-022 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 |
| TMDF210A-020 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 |
| TMDF250A-015 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 |
| TMDF250A-020 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 |
| TMDF250A-030 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 |
| TMDF300A-020 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 |
| TMDF400A-020 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |
| TMDF400A-030 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |
| TMDF500A-020 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 |
| TMDF500A-030 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 |
| TMDF600A-020 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 |
| TMDF600A-030 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 |

2)	S31: Function code

| No. |  | Function | 0 | 1 |
| --- | --- | --- | --- | --- |
| S31 Function code | Digit 1 | Remote switch/hotel card | Remote switch | Hotel card |
|  | Digit 2 | Air return temperature selection | Use air return temperature on control panel | Use air return temperature on wired controller |
|  | Digit 3 | Electric heater | Electric heater unavailable | Electric heater available |
|  | Digit 4 | AC/DC fan | AC fan | DC fan |

Note: When hotel card is used, connect the interlock switch to the control panel X8A.

3)	S32: Model code

Applicable to IDUs except TMDN***ACC

| S32 model code | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| TMDN*** (except ACC/D/E) | 0 | 0 | 0 | 0 | - | - | - | - |
| TMDN***ACD | 1 | 1 | 1 | 1 | - | - | - | - |
| TMDN***ACE | 1 | 1 | 1 | 0 | - | - | - | - |
| TMDN***AEB | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 |
| TMDH | 0 | 0 | 1 | 0 | - | - | - | - |
| TMCF | 1 | 0 | 1 | 1 | - | - | - | - |
| TMVW | 0（by default） | 0（by default） | 0（by default） | 0（by default） | - | - | - | - |
| TMDF | 0 | 1 | 1 | 0 | - | - | - | - |
| TMDP | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |

VIII. Precautions When Using/Maintaining Air Conditioner

1.	Precautions for air conditioner usage

Set a proper indoor temperature.

♦	Recommended temperature for cooling: 26~28°C; recommended temperature for heating: 18~23°C. Too high or too low indoor temperature can make people feel uncomfortable. If the set temperature is 1°C higher in cooling mode or 2°C lower in heating mode, 10% electricity could be saved.

Clean the filter screen.

♦	Clogged filter will severely affect the air supply efficiency and may lead to malfunction.

♦	If the air conditioner is not used for a long time, clean the filter thoroughly before running cooling or heating modes.

Open doors and windows as little as possible to reduce indoor and outdoor heat exchange.

♦	When cooling and heating, do not open doors and windows. If not necessary, do not open doors or exits to reduce indoor heat loss.

♦	To prevent hot air from entering the air conditioning room during cooling, set curtains or blinds on the windows to shield direct sunlight.

Ventilate as necessary.

♦	The long-term stagnation of indoor air, as well as the breath of personnel and the smell emitted by other objects, will cause indoor air pollution, so it is necessary to ventilate the indoor space in a timely manner to keep the indoor air fresh.

Effectively use the timer.

♦	When sleeping and going out, use a timer to keep the unit running for the necessary time to save power.

Do not touch the air conditioner with wet hand to prevent electric shock.

♦	Do not operate the wired controller or remote controller with wet hand, or splash water into the wired controller or remote controller.

Do not use air conditioner for special purposes such as food preservation, animal and plant keeping, precision instrument and artwork preservation, etc.

♦	Otherwise, the quality of these items will be affected.

Do not place indoor heating equipment under the IDU.

♦	Hot air may deform the suction grille of the IDU.

2.	Precautions for air conditioner maintenance

If the air conditioner is not to be used for a long time period:

♦	Run the air conditioner in air supply mode for 3 to 4 hours to completely dry it. Then, turn off the air conditioner and power off.

If the air conditioner is to be used after being left idle for a long time:

♦	Make sure that the unit is in stop status and the power is not connected. Then, clean the filter and the IDU body.

♦	Do not clean the IDU and ODU of air conditioner with water to avoid electric shock and fire.

♦	Use a soft cloth to wipe the IDU body. Do not use gasoline, benzene, dilute alkali solution, grinding powder, detergent and insecticide to clean the unit, which may cause damage.

♦	Confirm that the air inlet and outlet of the IDU and ODU are not blocked by sundries.

♦	Check whether the grounding wire is loose. Connect the power supply for at least 12 hours to keep the unit in standby state.

♦	Do not turn off the power during seasons when the air conditioner is frequently used.

Clean the filter:

♦	Remove the filter. Use a vacuum cleaner or water to clean it.

♦	If the filter is too dirty, use neutral detergent to brush.

♦	Do not clean with hot water (about 50°C or more) to avoid deformation.

♦	After cleaning with water, let the filter dry in a shady and well-ventilated place. Do not expose the filter to direct sunshine or dry it on fire.

3.	Troubleshooting non-air conditioner faults

If the phenomenon in the following table occurs during the use of the air conditioner, the user can troubleshoot these common and simple faults:

| Symptom | Analysis of Causes | Solution |
| --- | --- | --- |
| IDU fan does not operate | Room temperature higher (during heating) or lower than set temperature (during cooling) | Reset the temperature |
|  | Measure to prevent cold air supply upon turn-on in heating mode | Wait for about 4 minutes |
| Air conditioning unit does not work | Power supply is not on | Check and power on |
|  | Timed start function is set | Wait or cancel timed start |
|  | Main power supply fuse burnt | Replace the fuse |
| Too little cold air or insufficient hot air | The filter is too dirty | Clean or replace the filter |
|  | Air return outlet of the IDU is blocked | Remove obstacles |
|  | ODU is not well-ventilated |  |
| Remote controller display blurred or malfunctioning | Low battery | Replace with a new battery |
|  | The battery is not installed correctly | Reinstall correctly |
|  | Whether the unit is too far from the remote controller (over 6 m) | Close to the unit remote control |
|  | Whether the electronic ballast is started or shut down | Wait a moment |
| There is condensate water on the front panel of the IDU | High air humidity | Dehumidification |
| IDU stops running in heating mode | ODU frosting after long-term running of air conditioner in heating mode, it is defrosting | The IDU resumes running automatically after defrosting |
| Fan stops running in dry mode | Dehumidification is controlled by microcomputer. The start/stop of fan motor and compressor is determined by a special program. This is a normal phenomenon. | Auto recovery |

## 4. Troubleshooting air conditioner faults

If the problem cannot be resolved, contact local maintenance service personnel and record the fault code of the wired controller and remote controller.

When the remote controller is faulty, the corresponding indicator on the IDU panel blinks (once every 2.5s, each blink takes 1s):

| Times of blinks of the indicator | Fault name | Times of blinks of the indicator | Fault name |
| --- | --- | --- | --- |
| 1 | Entering coil temperature sensor fault | 2 | Md-coil temperature sensor fault |
| 3 | Leaving coil temperature sensor fault | 4 | Return air temperature sensor fault |
| 5 | Communication failure of IDU and ODU | 6 | Operating mode conflict |
| 7 | Water level alarm fault |  |  |
| Note: Wall-mounted units (TMVW) display failures via the indicator of running status; while units of other models via the indicator of defrosting. |  |  |  |
| IDU model | Fault indicator | IDU model | Fault indicator |
| TMCF | Defrosting indicator | TMVW | Run indicator |
| TMCS | Defrosting indicator | TWCD | Defrosting indicator |
| TMVX | Defrosting indicator |  |  |

IX. After-sales Service of Air Conditioning Unit

1.	After-sales service

After-sales services include repair, installation, maintenance, and reinstallation.

Installation should be carried out by dealers.

2.	Repair record

X. Names and Content of Hazardous Substances in Products

●	This product complies with the environmental protection requirements of the Measures for the Administration of the Restricted Use of the Hazardous Substances Contained in Electrical and Electronic Products.

●	Environmental protection service life: In the environmental protection service life, the user's normal use of this product will not cause serious pollution to the environment or cause serious damages to persons and properties. The service life is specified by TICA. The environmental protection service life is not equivalent to the service life of safe use.

●	Recycling: When this product is not needed or its service life ends, recycle it according to the related national regulations on recycling of waste electrical and electronic products. Do not discard it at will.

●	Names and content of hazardous substances in products

| Part name | Hazardous substance |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Plumbum (Pb) | Mercury (Hg) | Cadmium (Cd) | Hexavalent chromium (Cr(VI)) | Polybrominated Biphenyl (PBB) | Polybrominated Diphenyl Ether (PBDE) |
| Motor | Ο | Ο | Ο | Ο | Ο | Ο |
| Heat exchanger | Ο | Ο | Ο | Ο | Ο | Ο |
| Refrigerant | Ο | Ο | Ο | Ο | Ο | Ο |
| Pipeline fittings and valves | × | Ο | Ο | Ο | Ο | Ο |
| Screws, bolts, and other fasteners | Ο | Ο | Ο | × | Ο | Ο |
| Other metal parts | Ο | Ο | Ο | × | Ο | Ο |
| Controller and electrical components | × | Ο | Ο | Ο | Ο | Ο |
| Sponge | Ο | Ο | Ο | Ο | Ο | Ο |
| Foam | Ο | Ο | Ο | Ο | × | Ο |
| Other plastic parts | Ο | Ο | Ο | Ο | Ο | × |
| Rubber parts | Ο | Ο | Ο | Ο | Ο | Ο |
| Other printed matters | Ο | Ο | Ο | Ο | Ο | Ο |
| Accessories (remote controller, battery, etc.)* | Ο | Ο | Ο | Ο | Ο | Ο |
| This table is prepared according to the provisions of SJ/T 11364. Ο: It indicates that the content of this hazardous substance in all homogeneous materials in this part is below the limit requirement defined in GB/T 26572. ×: It indicates that the content of this hazardous substance in at least one homogeneous material in this part exceeds the limit requirement defined in GB/T 26572. Moreover, substitution cannot be implemented at present due to technical reasons, and it will be improved gradually along with technical progress in the future. *: It indicates that the environmental protection service life of the battery matched with the product is 2 years. The number in this identification indicates that the environmental protection service life of the product under the normal use status is 15 years. Some parts may also have the identification of environmental protection service life, and their environmental protection service life is subject to the number in the identification. The product configuration may be different due to different models or product improvements. The actual configuration of sold products should prevail. |  |  |  |  |  |  |